## CA Log
SAMC East Tower - Corrective Action Log (as of 9/26/2026)
CA # | Date Found | Subcontractor | Area / Location | Deficiency | Class | Due | Status | Date Closed | Package
CA-0601 | 2026-06-09 | Suncoast Concrete Forming LLC | Grid B-4 footing | Excavation 6 ft deep, no trench box, 2 workers inside | Imminent danger | 2026-06-09 | Closed | 2026-06-09 | SITE
CA-0602 | 2026-06-16 | Suncoast Concrete Forming LLC | Grid D-2 | Spoil pile at edge of footing excavation | Other than serious | 2026-06-23 | Closed | 2026-06-18 | SITE
CA-0603 | 2026-06-30 | Keel Crane Services, Inc. | Tower crane base | Monthly crane inspection record missing from site file | Serious | 2026-07-01 | Closed | 2026-07-01 | SITE
CA-0701 | 2026-07-14 | Suncoast Concrete Forming LLC | Level 2 deck | Floor opening 3x4 ft uncovered at shaft | Imminent danger | 2026-07-14 | Closed | 2026-07-14 | STRUCT
CA-0702 | 2026-07-21 | Tidewell Steel Erectors LLC | Level 3 east | Connector not tied off at 12 ft during bolting | Imminent danger | 2026-07-21 | Closed | 2026-07-21 | STRUCT
CA-0703 | 2026-07-28 | Tidewell Steel Erectors LLC | Laydown yard | Damaged wire rope sling in use | Serious | 2026-07-29 | Closed | 2026-07-30 | STRUCT
CA-0801 | 2026-08-11 | Mangrove Electric Co. | Temp power panel TP-3 | Missing GFCI on temporary receptacle | Serious | 2026-08-12 | Closed | 2026-08-12 | MEP
CA-0802 | 2026-08-18 | Tidewell Steel Erectors LLC | Level 4 | Ladder used above 6 ft without approval | Other than serious | 2026-08-25 | Closed | 2026-08-22 | STRUCT
CA-0901 | 2026-09-08 | Sterivault Containment LLC | Corridor L1 connector | ICRA barrier gap at deck, no negative pressure log for 2 days | Imminent danger | 2026-09-08 | Closed | 2026-09-08 | CONNECT
CA-0902 | 2026-09-15 | Heronfield Mechanical, Inc. | Mech room L2 existing | Hot work (brazing) without permit next to occupied area | Serious | 2026-09-16 | Open |  | CONNECT
CA-0903 | 2026-09-22 | Tamaris Drywall & Acoustics, Inc. | Corridor L2 | Debris cart uncovered on patient route | Other than serious | 2026-09-29 | Open |  | CONNECT
CA-0904 | 2026-09-23 | Mangrove Electric Co. | Electrical room L1 existing | Panel cover removed, energized parts exposed, no barricade | Serious | 2026-09-24 | Open |  | CONNECT
CA-0905 | 2026-09-24 | Kestrel Fire Protection, Inc. | Level 5 | Sprinkler impairment without impairment notice | Serious | 2026-09-25 | Open |  | MEP
CA-0906 | 2026-09-25 | Suncoast Concrete Forming LLC | Level 5 deck edge | Guardrail mid-rail missing 20 ft | Other than serious | 2026-10-02 | Open |  | STRUCT